## Sheet1
University of Arizona- Satellite Tower Survey Information
System | Towers | Make | Metal | Est'd. System Volume (Gal) | Est'd Annual MU (Gal) | Tonnage | Controller | Chemistry | Closed Loop
Harshbarger | 2 Towers- 1 System | SPX Marley, 6x6' | Galv | 1500 | 1000000 |  | Lakewood 140, cond probe only | 2 drums ?? | Y
Roof Access Only
Chavez | 1 System | Evapco, 15x10' | Galv | 1200 | 750000 |  | Lakewood with cond only | 1 drum | Y
Ground Access
Roy Place | 1 system | Remsa 5' Diam | Fiberglass | 1000 | 750000 | Cond Pump: HP-50, 1775 RPM | Old Aquatrac controller | 1 drum | Y
Roof Access Only
Veterinary Medicine | 1 System |  |  | 500 | 750000 |  | LMI controller | 1 drum | N
| Ground Access | 3x2' Tower | Galv
AML | 2 Systems | Marley 6'x6' Tower | Galv | 1000 | 750000 | Cond Pump: 3HP, 3450 RPM | Old Lakewood, analog | 1 drum | Y
| Ground Access | Remsa 5" Diam | Fiberglass | 500 | 500000 | "" |  | 1 drum | Y
USA | 1 System | (2) towers | Galv | 1300 | 1250000 | two 300 ton York Chillers; Plate/frame HX | Lakewood with cond only | 1 drum | Y
Ground Access
USB | 1 system | 2 BAC towers | Galv | 2000 | 1500000 | 10 total DX units (35 tons ea. ?) 350 total | Lakewood with cond only | Inhib + Glut | N
Roof access
Marshall | 2 Systems | two BAC fluid coolers | Galv | 2000 | 1000000 | 5 Intellipaks (50 tons ea?) 250 tons total | (2) LMI DC4500 controllers | 1 drum | Y
Roof access
Babcock | 1 System | 2 small BAC's | Galv | 1500 | 1250000 | (2) 150 ton Carriers | Lakewood with cond only | 1 drum | Y
Roof access
VDL | Assume same as Babcock |  |  | 1500 | 1250000
Additonal Notes:
Tower cleanings done in house. No consistent schedule. |  |  | TOTAL: | 14000 | 10750000